# HAVANT BOROUGH COUNCIL

Town & Country Planning Act 1990

CONSULTATION ON PLANNING APPLICATION

### MEMORANDUM

| From: | Environmental Health | To: | Development Control |
| --- | --- | --- | --- |
| Our Ref: | CONS/25/00194 | Your Ref: | APP/24/00157 |
| EH Case Officer Ext: | 6569 | Date: | 13.02.2025 |

| DC Case Officer: | Mr D Eaves |
| --- | --- |
| DC Case Officer Ext: | 6549 |
| Application Number: | APP/24/00157 |
| Site Address: | Oak View Residential Care Home, 49 Beach Road, Hayling Island, PO11 0JB |
| Proposed Development: | Proposed erection of a first-floor side (south) extension and the provision of three additional bedrooms (Class C2) |

Observations / Comments:

We have no issue with the principle of the development.  However, it is important that the development is delivered in a manner compatible with the site’s location and existing neighbouring land uses.

In line with the ‘Agent of Change’ principle, the responsibility for managing the impact of any change lies with the person or organisation introducing it, we request that any approval is subject to the following conditions to ensure that:

- Potential impacts from the repositioning of existing plant are appropriately controlled.

Building services Plant Noise

It is critical to ensure that noise from such plant and equipment is adequately controlled to minimise the risk of adverse impacts on occupants of existing dwellings in the vicinity, as well as future residents of the development.

Accordingly, we recommend the imposition of the following condition:

| Condition 1: |  | Noise emitted from any fixed building services plant and equipment shall be controlled to at least 5 dB(A) below the lowest representative existing background sound level, when assessed in accordance with BS 4142:2014+A1:2019, at a position 1 metre outside any habitable window of any residential or other noise-sensitive property. This criterion applies to the total contribution of noise from all plant and equipment associated with the development operating during any given period. Prior to commencement of construction works above ground, full details shall be submitted to and approved in writing by the Local Planning Authority, demonstrating how noise will be controlled to meet this condition. The scheme shall be fully implemented in accordance with the approved details and thereafter retained and maintained for its designated purpose. The baseline noise survey must cover a period sufficient to faithfully represent the prevailing noise climate at the nearest noise-sensitive premises during the plant’s operating hours. In most cases this will cover survey during the weekday and weekend period. The typical minimum background sound level should be defined as the 10th percentile value for the daytime (07:00-23:00) and night-time (23:00-07:00) when the plant may operate. The assessment must include valid predictions and valid assessment of any acoustic features. |
| --- | --- | --- |
| Reason: |  | To protect the existing noise climate and the amenity and quality of life of residents in the local area from undue noise disturbance. |  |  |