Redevelopment of Colt Industrial Estate, Havant

Drainage Maintenance

Introduction

All of the drainage constructed as part of this project will be maintained by a management company put in place by Drew Smith Ltd.

Maintenance schedules based on the following will be included in the operation and maintenance manual to be prepared for handover to the management company at the point that the project is completed.  The only anticipated change to the following will be where the manufacturer of an item has a different maintenance recommendation for that specific item in which case the manufacturers recommendation will be adopted.

Drainage System Generally

| Maintenance schedule | Required action | Recommended Frequency |
| --- | --- | --- |
| Regular maintenance | Inspect and identify any areas that are not operating correctly. If required, take remedial action | Monthly for three months then annually |
|  | Remove debris from the catchment surface (where it may cause risks to performance) | Annually, after leaf fall or more frequently if required. |
|  | Remove debris from gullies | Annually in late summer |
| Remedial actions | Repair/rehabilitate or clear all inlets, outlets, overflows, and pipes | As required |

Maintenance activities should be detailed in the health and safety plan and a risk assessment should be undertaken.

Cellular Tanks Operation & Maintenance Requirements

Regular inspection and maintenance is required to ensure the effective long-term operation of below ground modular storage systems.

Specific maintenance needs of the system should be monitored, and maintenance schedules adjusted to suit requirements.

Modular systems – operation and maintenance requirements

| Maintenance schedule | Required action | Recommended Frequency |
| --- | --- | --- |
| Regular maintenance | Inspect and indentify any areas that are not operating correctly. If required, take remedial action | Monthly for three months then annually |
|  | Remove debris from the catchment surface (where it may cause risks to performance) | Monthly |
|  | For systems where rainfall infiltrates into the tank from above, check surface of filter for blockage by sediment, algae, or other matter; remove and replace surface infiltration medium as necessary | Annually |
|  | Remove sediment from pretreatment structures and/or internal forebays | Annually, or as required |
| Remedial actions | Repair/rehabilitate inlets, outlets, overflows, and vents | As required |
| Monitoring | Inspect/check all inlets, outlets, overflows, and vents to ensure that they are in good condition and operating as designed | Annually |
|  | Survey inside of tank for sediment buildup and remove if necessary | Every five years or as required |

Maintenance activities should be detailed in the health and safety plan and a risk assessment should be undertaken.

Interceptors Operation & Maintenance Requirements

Ease of access for maintenance and inspection is essential. In particular, lids should be kept as lightweight as practicable.

A routine inspection programme should be established for each unit. This should be based on the volume or load of the contaminants of concern, the frequency of releases of contaminants, and the nature of the area being drained. During the first 30 days after installation, sub-surface pre-treatment units should be visually inspected after every rainfall event and the amount of deposition measured to give the operator an idea of the expected rate of sediment deposition. After this initial period, systems should be inspected at least every six months to verify the appropriate level of maintenance. During these inspections, the floating debris and solids should be removed and the sump cleaned out using a conventional sump vacuum cleaner. In most situations, the units should be cleaned out at least annually.

Litter picking at site should be frequent, as rubbish is detrimental to the operation of the facility and the appearance of the site. Frequent street sweeping in the catchment area of a filtration system increases the time interval in which the sedimentation facility has to be cleaned out and reduces the amount of fine suspended solids that can potentially clog the filter media.

Proper disposal of oil, solids and floating debris removed from pre-treatment components must be ensured, and the environmental regulator can offer advice where there are any doubts concerning disposal options. A small portion of water will be removed along with the pollutants during the clean-out process, which should be considered when costing sediment disposal processes.

Harmful vapours may develop in sub-surface filtration or hydrodynamic separation units, as hydrocarbons may remain there for extended periods of time. Appropriate testing for harmful vapours and venting should be undertaken whenever access for maintenance is required.

Pre-treatment systems: operation and maintenance requirements

| Maintenance schedule | Required action | Frequency |
| --- | --- | --- |
| Regular maintenance | Removal of litter and debris | Six monthly |
| Occasional maintenance | Change of filter media | As required |
|  | Removal of sediment, oil, grease and floatables | As required |
| Remedial actions | Replacement of malfunctioning parts | As required |
| Monitoring | Inspect for evidence of poor operation | Six monthly |
|  | Inspect filter media and establish appropriate replacement frequencies | Six monthly |
|  | Inspect sediment accumulation rates and establish appropriate removal frequencies | Monthly during first half year of operation, then every six months |

For oil/water separators, the following items should be undertaken every six months as a minimum:

- check volume of sludge

- check thickness of light liquid

- check function of automatic closure device

- empty the separator if required

- check the coalescing material and clean or change if necessary (Class 1 only)

- check the function of the warning device (if fitted).

General inspection of oil/water separators should occur at a maximum frequency of five years, and should cover the following:

- watertightness of system

- structural condition

- internal coatings

- in-built parts

- electrical devices and installations

- checking of adjustment of automatic closure devices

It is of key importance that the separator is filled with clean water before it is put into operation and each time after it is emptied for maintenance. Failure to do so will cause the separator to malfunction until stormwater builds up the required permanent water level in the facility. It is possible to fit an alarm to separators that will indicate when the collected oil volume is at a maximum, and this may be a regulatory requirement.

Maintenance activities should be detailed in the Health and Safety Plan and a risk assessment should be undertaken.

Permeable Paving Operation & Maintenance Requirements

Regular inspection and maintenance is important for the effective operation of pervious pavements. The facility should be inspected regularly, preferably during and after heavy rainfall to check effective operation and to identify any areas of ponding.

Pervious surfaces need to be regularly cleaned of silt and other sediments to preserve their infiltration capability. Manufacturers’ recommendations should always be followed.

A brush cleaner, which can be a lorry-mounted device or a smaller precinct sweeper, should be used and the sweeping regime should be as follows:

- End of winter (April) – to collect winter debris.

- Mid-summer (July/August) – to collect dust, flower and grass-type deposits.

- After autumn leaf fall (November).

Care should be taken in using vacuuming equipment to avoid removal of jointing material. Any lost material should be replaced.

If reconstruction is necessary, the following procedure should be followed:

- Lift surface layer and laying course.

- Remove any geo-textile filter layer.

- Inspect sub-base and remove, and replace if required.

- Renew any geo-textile layers.

- Renew laying course, jointing material and concrete block paving.

The reconstruction of failed areas of concrete block pavement should be less costly and disruptive than the rehabilitation of continuous concrete or asphalt porous surfaces due to the reduced area that is likely to be affected. Materials removed from the voids or the layers below the surface may contain heavy metals and hydrocarbons and may need to be disposed of as controlled waste. Sediment testing should be carried out before disposal to confirm its classification and appropriate disposal methods.

Pervious pavement operation and maintenance requirements

| Maintenance schedule | Required action | Frequency |
| --- | --- | --- |
| Regular maintenance | Brushing | Once a year, after autumn leaf fall, or reduced frequency as required, based on site-specific observations of clogging or manufacturer’s recommendations – pay particular attention to areas where water runs onto pervious surface from adjacent impermeable areas as this area is most likely to collect the most sediment |
| Occasional maintenance | Stabilize and mow contributing and adjacent areas | As required |
|  | Removal of weeds or management using glyphosphate applied directly into the weeds by an applicator rather than spraying | As required – once per year on less frequently used pavements |
| Remedial actions | Remediate any landscaping which, through vegetation maintenance or soil slip, has been raised to within 50mm of the level of the paving | As required |
|  | Remedial work to any depressions, rutting, and cracked or broken blocks considered detrimental to the structural performance or a hazard to users, and replace lost jointing material | As required |
|  | Rehabilitation of surface and upper substructure by remedial sweeping | Every ten to fifteen years or as required (if infiltration performance is reduced due to significant clogging) |
| Monitoring | Initial inspection | Monthly for three months after installation |
|  | Inspect for evidence of poor operation and/or weed growth – if required, take remedial action | Three-monthly, 48hrs after large storms in first six months |
|  | Inspect silt accumulation rates and establish appropriate brushing frequencies | Annually |
|  | Monitor inspection chambers | Annually |

Maintenance activities should be detailed in the Health and Safety Plan and a risk assessment should be undertaken.

Monsoon Drain Operation & Maintenance Requirements

Regular inspection and maintenance is important for the effective operation of channels as designed.

This is an Ordinary Watercourse and as such the responsibilities of a Riparian Owner with a duty to maintain the channel apply.

Channel operation and maintenance requirements

| Maintenance schedule | Required action | Frequency |
| --- | --- | --- |
| Regular maintenance | Remove litter and debris | Monthly, or as required |
|  | Remove any vegetation | Monthly at start, then as required |
|  | Inspect inlets, outlets, and overflows for blockages and clear if required | Monthly |
|  | Inspect inlets and facility surface for silt accumulation, establish appropriate silt removal frequencies | Monthly initially, then as required |
| Monitoring | Inspect inlets, outlets and overflows for blockages, and clear if required | Monthly |
|  | Inspect all concrete for damage, cracking etc and arrange repair as required | Annually |

Maintenance activities should be detailed in the health and safety plan and a risk assessment should be undertaken.