## Sheet1
Hampshire County Council's Flood and Water Management Team have created this template to assist developers when seeking planning permission for new sites.
In order for the team to be able to act as a statutory consultee for surface water drainage for major planning applications ALL of the following information is required.
This check list is designed to help developers provide the correct information and reduce time spent by HCC searching for details we require.
FOR ALL APPLICATIONS WE ARE ASKED TO COMMENT ON WE WILL NEED THE FOLLOWING INFORMATION - PLEASE FILL IN THIS FORM AND SUBMIT WITH ANY SURFACE WATER CONSULTATIONS
| Information required: | Included | Document chapter/page number where information can be viewed
1 | Background information on the proposed design. Including proposal; site; plans of surface water drainage and any SuDS featured in the scheme | Yes | Drawing No CES482/01 - Shows Design Network along with locations of Flow Control and SUDS Treatment (Downstream Defender)
2 | Evidence that the applicant understands the sensitivity of discharge points relating to the receiving water body. Where this is main river or discharging through contaminated land the LPA may have to consult the Environment Agency (EA) | Yes | Percolation Test Failed, No Watercourse nearby to connect therefore only viable solution was connection to existing Surface Water Sewer in Highway just outside of development site boundary. See CES482/01 for connection location point.
3 | Evidence of and information on the existing surface water flow paths of undeveloped (greenfield) sites |  | Site was previously developed and had an existing surface water network, so not greenfield.
4 | Evidence of and information on the existing drainage network for previously developed (brownfield) sites |  | The new strategy proposes all existing surface water systems be removed, including a new main combined sewer utility connection. We therefore propose there is no need to submit details of existing site drainage.
5 | Identification of and information on areas that may have been affected by failures in the existing drainage regime |  | No failures reported on exiting network. Exising network servecing developments around the site with no known failiurs reported at time of netowrk design. New onsite network to replace old as new development is a completely new layout to exiting.
6 | Evidence that the proposed drainage will follow the same pattern as the existing. This avoids directing flow to other locations. | Yes | New drainage network has been designed to capture all of the developments site run off. The site is completely impermeable in its existing and proposed condition therefore no change and new drainage network is designed to cope with the total area. Gullies have been included in highway to mitigate run off from highways onto adjoining streets and downpipes capture all roof run off which goes direct into new network.
7 | Information evidencing that the correct level of water treatment exists in the system in accordance with the Ciria SuDS Manual C753 | Yes | Site is treated by Downstream Defender (See Downstream Defender Information Document Attached). This treatment method will separate siltation and oil particles with clean water discharged from unit to the flow control manhole for discharge from site. Attenuation tank designed post treatment to lower risk of siltation within tank.
8 | Where infiltration is used for drainage, evidence that a suitable number of infiltation tests have been completed. These need to be across the whole site; within different geologies and to a similar depth to the proposed infiltration devices. Tests must be completed according to the BRE 365 method or another recognised method including British Standard BS 5930: 2015 |  | Percolation Test were carried out on site by the client in accordance to BRE365 method but all test failed therefore unable to use filtration process as method of SUDS.
9 | If not using infilitration for drainage - Existing and proposed run-off rate calculations completed according to a suitable method such as IH124 or FEH. Information is available from UK Sustainable Drainage: Guidance and Tools. Calculations must show that the proposed run off rates do not exceed the existing run-off rates. This must be shown for a one in one year event plus climate change and a one in one hundred year event plus climate change. |  | All caluclations are found in Micro Drainage Network Details. Wallingford Greenfield Run Off rate calculator PDF shows greenfied run off rates for development site. However the development site is currently brownfield therfore flow control designed for 50% betterment of brownfield run off rate.
10 | If not using infiltration for drainage - Existing and proposed run-off volume calculations completed according to a suitable method such as IH124 or FEH. Calculations must show that, where reasonably practical, runoff volume should not exceed the greenfield runoff volume for the same event. This must be shown for a 1 in 100 year, 6 hour rainfall event |  | Achieving Greenfield run off rates on this sit would not be possible given that there will be not enough available room to facilitate an attenuation tank needed to attenuate the water if limited to Greenfield run off rates. New network design for 50% betterment of Brownfield run off rate given the site is an existing Brownfield site.
11 | Evidence that enough storage/attenuation has been provided without increasing the runoff rate or volume. This must be shown for a 1 in 100 year plus climate change event | Yes | See Micro Drainage Network Details Provided with Design. Calculations have been done for 1 in 100 year + CC and 1 in 1 year + CC showing no flooding occurs during both extreme events. Additional storage was required therefore an offline attenuation tank was design to increace storage capacity prior to dischage from the site boundary.
12 | Evidence that runoff exceeding design criteria has been considered. Calculations and exceedance flow diagram/plans must show where above ground flooding might occur and where this would pool and flow. |  | Drainage system has been design to capture all run off from the site. Given the site is all impermable, all non roofspcace run off will be captured via gullies at low points on site to avoid any ponding. As the whole site is considered impermable in netowrk design it is not possible for run off to exceed what has been considered within the design.
13 | Maintenance regimes of entire surface water drainage system including individual SuDS features, including a plan illustrating the organisation responsible for each element. Evidence that those responsible/adopting bodies are in discussion with the developer. For larger/phased sites, we need to see evidence of measures taken to protect and ensure continued operation of drainage features during construction. |  | Client must provide their own maintenance schedule but as a guideline the minimum requirement is to follow manufacturers maintenance guidelines with the Hydrobreak, Attenuation tank and Downstream Defender.
14 | Evidence that Urban Creep has been considered in the applicationm and that a 10% increase in inpermeable area has been used in calculations to account for this. |  | The Suface network Design includes all the area within the site boundary therfore an additonal 10% will not be possible. All of the current site is imprmable therefore would not be possible to increase impermable area by 10%.
15 | Did you take advantage of Hampshire County Council's Pre-Application advice service (details below)? If so, please insert your pre-application reference number here. | Y/N | Pre application number - GEN/17/01374
SuDS Manual
http://www.ciria.org/Memberships/The_SuDs_Manual_C753_Chapters.aspx
Guidance for Climate Change percentages
http://www.susdrain.org/files/resources/briefings/1610_briefing_climate_change_briefing_note.pdf
British Standard for Infiltration tests BS 5930: 2015
http://hantsfilewebservices.it2000.hants.gov.uk/linkviewer/LinkViewer.aspx?PIDv1=90%203%20ICM8%20ICMNLSDB10%20DOC%5FBIN%5F0159%2026%20A1001001A17E25B22432G7509818%20A17E25B22432G750981%2014%201177/LinkViewer.aspx
HCC's Pre-application Service
http://documents.hants.gov.uk/flood-water-management/Surfacewaterandpre-applicationguide-Nov2015.pdf
UK Sustainable Drainage: Guidance and Tools
http://www.uksuds.com/
Note on F7: cxecvw: