Surface Water Maintenance
This document sets out the principles for the long-term management &

maintenance of the surface water network within the proposed development and provides information in order to clear planning condition 20 which is to ensure that the proposed development does not flood and ensure future maintenance of the surface water drainage system.

Surface Water System Maintenance

The following maintenance should be carried out every six months by experienced

personnel:

Assess the depth of accumulated silt and keep a detailed log of when the

chamber is inspected.

Parking area gullies to be cleaned

Storm pipes to be inspected and jetted where required.

Flow Control Chamber

Key Maintenance Requirements:

The hydraulic vortex flow control unit has no moving parts and is self-activating, requiring minimal maintenance.

After initial installation, it is recommended that the unit be inspected monthly for three months.

Thereafter the manhole chamber and control device should be inspected at least every six months to verify the condition and operation of the unit and check for blockages within the inlet of the chamber and of the flow control device.

During these inspections, accumulated silts should be removed and the sump cleaned out using a conventional sump vacuum cleaner.

Flow Controls are fitted with a pivoting by-pass door, which allows the manhole chamber to be drained down should blockages occur.
Cellular Attenuation
Key Maintenance Requirements:

Regular inspection of silt traps, manholes, pipework and pre-treatment devices, with

removal of sediment and debris as required.

Regular inspection and maintenance is required to ensure the effective long-term operation

of below ground modular storage systems.

Maintenance responsibility for systems should be placed with either a responsible

organisation such as a management company.
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