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Dear Sirs,

Proposal: Single storey rear extension and front infill extension. New cladding and render to front of property.
Site: 73 Linkenholt Way, Havant, PO9 4AS.
APP/17/00416
Thank you for your letter of 21/04/2017.

Please find attached a plan of the sewer records showing the approximate position of a public foul sewers within the site.
· No works parallel to the 225mm foul sewer within 500mm (in plan).
· No development or new tree planting should be located within 3 metres either side of the centreline of the public foul sewer (300mm).

· All existing infrastructure should be protected during the course of construction works.
· No new soakaways should be located within 5 metres of a public foul sewers.
Furthermore, due to changes in legislation that came in to force on 1st October 2011 regarding the future ownership of sewers it is possible that a sewer now deemed to be public could be crossing the above property. Therefore, should any sewer be found during construction works, an investigation of the sewer will be required to ascertain its condition, the number of properties served, and potential means of access before any further works commence on site.
The applicant is advised to discuss the matter further with Southern Water, Sparrowgrove House Sparrowgrove, Otterbourne, Hampshire SO21 2SW (Tel: 0330 303 0119) or www.southernwater.co.uk”.
Southern Water requires a formal application for any new connection to the public foul sewer to be made by the applicant or developer. 

We request that should this application receive planning approval, the following informative is attached to the consent:

“A formal application for connection to the public sewerage system is required in order to service this development, please contact Southern Water, Sparrowgrove House Sparrowgrove, Otterbourne, Hampshire SO21 2SW (Tel: 0330 303 0119) or www.southernwater.co.uk”.
It is the responsibility of the developer to make suitable provision for the disposal of surface water. Part H3 of the Building Regulations prioritises the means of surface water disposal in the order

a       Adequate soakaway or infiltration system

b       Water course

c        Where neither of the above is practicable sewer

Southern Water supports this stance and seeks through appropriate Planning Conditions to ensure that appropriate means of surface water disposal are proposed for each development. It is important that discharge to sewer occurs only where this is necessary and where adequate capacity exists to serve the development. When it is proposed to connect to a public sewer  the prior approval of Southern Water is required.

Yours sincerely

Claire Smith
Developer Services 
Southern Water Sparrowgrove House Otterbourne Winchester Hampshire SO21 2SW www.southernwater.co.uk
Southern Water Services Ltd  Registered Office: Southern House Yeoman Road Worthing BN13 3NX Registered in England No.2366670
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