To:  Aaron Wright

From:  Mike Smith

Date: 28th August 2012

Ref:  APP/12/00681

Site Address: 75 Lovedean Lane, Waterlooville

Proposed Development: Installation of extract flue in timber enclosure on flat roof to rear at first floor level.

I am writing in connection to the above application, following a noise report submitted by Mr Garry Hutchinson of GL Hearn Limited in his email of 21st August.

The applicant states in their report that when measured according to BS4142, the following noise levels from plant equipment are measured at the nearest residential property:

07:00 – 23:00 = -3dB

23:00 – 07:00 = +2dB

I would question however whether an acoustical correction factor of +3dB should have been added to the calculations as according to Figure 7.2 of Appendix B, the majority of the units are wall mounted, which means they would be up against one reflective surface.

Usually, Environmental Health would request the following, standard, noise condition relating to noise from plant/equipment:

“Noise resulting from the use of any/all plant, machinery or equipment shall not exceed a level of 5dB(A) below the existing lowest background noise level on the sites boundaries during the time of operation or 10dB(A) below if there is a particular tonal quality, when measured according to British Standard BS4142-1997.”

The Applicant’s report however demonstrates that they are not able to comply with this requirement.
I would therefore recommend that additional acoustical measures are carried out by the applicant to enable them to comply with this requirement.

