HAVANT  BOROUGH  COUNCIL

Town & Country Planning Act 1990

CONSULTATION ON PLANNING APPLICATION

MEMORANDUM

	  From: 
	 Environmental Health
	  To: 
	 Development Control

	
	 
	
	

	  Our Ref: 
	 CONS/25/xxxx
	  Your Ref: 
	 APP/25/00432

	
	
	
	

	  EH Case Officer Ext:
	 
	  Date: 
	 5 August 2025



	  DC Case Officer:
	 Lesley Wells

	  Application Number:
	 APP/25/00432

	  Site Address: 
	 37b Park Parade, Leigh Park, Havant

	Proposed Development: 
	Proposed change of use from Commercial, Business and Service (Use Class E) to Dwellinghouses (Use Class C3). First floor to be converted to 7no Apartments, Comprising a mixture of 1 bed, 2 bed and 3 bed dwellings.



Observations / Comments:
We have no objection in principle to the proposed development.  However, to ensure the development provides a reasonable standard of amenity for future occupants of the apartments while protect the amenity of existing residents in the local area from undue disturbance we recommend the following conditions be attached to the planning consent:
Control of Re-Radiated Noise from the Gymnasium and Dance Studio (Use Class E(d))
	Condition X:
	Appropriate mitigation measures shall be implemented, retained and maintained to control the transmission of airborne noise and structure-borne noise from the operation of the ground floor gymnasium and dance school.  These measures must ensure that noise levels within any residential habitable areas do not exceed the following criteria:
Airborne Noise (e.g. amplified music, instructor voice):
Noise from health and fitness activity shall not exceed curve G15 (Leq,5min) during the daytime and curve G10 at night.
Impact Noise (e.g. weight drops):
Noise from health and fitness activity shall not exceed curve G20 (Lmax,F) during the daytime and curve G15 at night.
For the purposes of this condition, “daytime” is defined as 07:00 to 23:00 hours and “night-time” as 23:00 to 07:00 hours.

	Reason:
	To protect the amenity and quality of life of occupants of the apartment from undue noise disturbance. 



Sound Insulation between Ground and First-Floor Residential Elements
Approved Document E (ADE) ‘Resistance to the passage of sound’ of the Building Regulations 2010 (as amended) sets out ‘minimum’ legal standards for buildings’ for resistance to the passage of sound.  The performance standards in tables 1a and 1b are applicable to walls, floors, and stairs separating spaces used for normal domestic purposes.  The document makes it clear that a higher standard of sound insulation may be required between spaces used for normal domestic purposes and those for communal or non-domestic purposes.  In these cases, the appropriate level of sound insulation will depend on the specific operational characteristics of the ground floor uses.  Accordingly, we recommend imposition of the following condition:
	Condition X:
	Noise from all fixed mechanical plant, equipment and operational activities associated with the ground floor commercial premises shall be controlled so they do not exceed the following Noise Rating (NR) levels within any habitable room of the residential accommodation above the premises:
· NR20 Leq,5min or NR 25 LFmax during daytime hours (07:00 to 23:00)
· NR15 Leq,5min or NR 20 LFmax during night-time hours (23:00 to 07:00)
Compliance shall be demonstrated through measurement in accordance with the guidance set out in the Association of Noise Consultants (ANC) document ‘Measurement of Sound Levels in Buildings, Version 1.0, June 2020’ or prediction using valid design stage prediction methods.

	Reason:
	To protect the amenity and quality of life of occupants of the apartments from undue noise disturbance. 


External Noise Intrusion into Apartments / Internal Amenity
	Condition X:
	Prior to occupation of the development, acoustic commissioning testing shall be carried out by an ANC or IOA accredited organisation to demonstrate compliance with the following internal noise criteria, while meeting the statutory requirements of Approved Document F (Ventilation) and Approved Document O (Overheating) of the Building Regulations:

	
	· Living Rooms: 
· Bedrooms: 
· Bedrooms:
	· 35 dB LAeq,16hr (07:00 to 23:00)
· 30 dB LAeq,8hr (23:00 to 07:00)
· 45 dB LAFmax not to be exceeded more than 10 times per night

	
	The commissioning protocol shall be agreed in writing with the Local Planning Authority prior to testing, and the results shall be submitted to and approved in writing with the Local Planning Authority before the occupation of the scheme.  

	Reason:
	To verify that the as-built development provides a reasonable standard of amenity for future occupants of the homes.




Building Services Plant Noise
It’s not clear what, if any building services plant, such as ASHPs, will be introduced as part of the development.  If any plant is introduced, then this must be adequately controlled to minimise the risk of adverse impacts on occupants of existing dwellings in the vicinity, as well as future residents of the development.  Accordingly, we recommend the imposition of the following condition:

	Condition X:
	Noise emitted from any fixed building services plant and equipment shall be controlled to at least 5 dB(A) below the lowest representative existing background sound level, when assessed in accordance with BS 4142:2014+A1:2019, at a position 1 metre outside any habitable window of any residential or other noise-sensitive property.  This criterion applies to the total contribution of noise from all plant and equipment associated with the development operating during any given period.

	Reason:
	To protect the existing noise climate and the amenity and quality of life of residents in the local area from undue noise disturbance. 



I trust my comments are clear, but please contact me if you require any clarification or wish to discuss any point further and I will be happy to assist.
Yours sincerely,
Laurence Evans
Pollution Team Leader
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