APP/26/00332 Padnell Grange, Padnell Road, Waterlooville, PO8 8ED

B. 
For fire safety and means of escape, all 1st floor bedrooms should have either means of escape windows or escape via a protected hallway which should have an REI of 30 minutes. B1
With regards to surface spread of flame, it is noticed there are a number of plots that could potentially exceed the allowable unprotected area namely plots 55-58, 59-61, 62-63, 64-65, 66-68, 72-74, 75-77. The Principal Designer should consider the area of cladding/material used on the returns in unison with the window sizes, as it appears it could exceed the UPA with the notional boundaries at approx. 1m. B4. 
Plots 1-4, 78-81, where the stair discharges into the ground floor Kitchen/dining area, inner room situations have been created to the 1st floor. This will impact requirement B1 meaning means of escape windows will be required at 1st floor, the Principal Designer should consider any planning conditions with regards to openable windows at 1st floor. B1.
Plots 5-15. (Flats) 
· The Principal Designer should consider the addition of a vent to the head of the protected stair. B1
· The Principal designer should consider that no point of the flats should exceed 45m from the pumped appliance, if 45m is exceeded then mains should be provided. B5.
C. 
From a desktop search, the area looks to be in a 1-3% radon affected area. The Principal Designer should consider whether Radon protective measures are required. 
H.
There appears to be no provisions for solid waste storage for the dwelling houses. H6

